**Price Adjustable Heavy Duty Gym Grille**

**Division 23 – Heating, Ventilating, and Air Conditioning**

**Section 23 37 13 – Diffusers, Registers, and Grilles**

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

**PART 1 – GENERAL**

* 1. **Section includes**:
1. Adjustable Heavy Duty Gym Grilles.
	1. **Related Requirements**
2. Section 01 30 00 – Administrative Requirements
3. Section 01 40 00 – Quality Requirements
4. Section 01 60 00 – Product Requirements
5. Section 01 74 21 – Construction/Demolition Waste Management and Disposal
6. Section 01 78 00 – Closeout Submittals
7. Section 01 79 00 – Demonstration and Training
	1. **Reference Standards**
8. All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.
9. ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets
10. ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces
11. ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints
12. ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes
13. ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments
14. ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

**1.04 Submittals**

1. See Section 01 30 00 – Administrative Requirements for submittal procedures.
2. Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.
3. Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.
4. Project Record Documents: Record actual locations of units and control components.
5. Operation and Maintenance Data: Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data (if applicable).
6. Warranty: Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.
7. Maintenance Materials: Furnish the following for Owner's use in maintenance of project.

**1.06 Quality Assurance**

1. Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

**1.07 Warranty**

1. See Section 01 7800 - Closeout Submittals, for additional warranty requirements.
2. Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

**PART 2 – PRODUCTS**

**2.01 Heavy Duty Gym Grille**

1. Basis of Design: Price Industries, Inc.
2. Single Deflection Adjustable Heavy Duty Gym Grille: Model 910
3. Double Deflection Adjustable Heavy Duty Gym Grille: Model 920

**2.02 Single Deflection Heavy Duty Adjustable Gym Grille**

1. Description:
	1. Furnish and install Price Model 910 heavy duty gym grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.
2. Construction:
	1. The grille blades and border shall be steel construction.
	2. The 14 gauge steel border shall have smooth contours to reduce the possibility of injury to occupants when installed in a gymnasium. The grille shall be suitable for surface mounting with 1-1/4 inch flat border.
	3. Grilles blades shall be single deflection, individually adjustable louver type, and shall be adjustable from +/- 45 degrees deflection, with 1/2 inch on center blade spacing.
	4. The grille blade orientation shall be (**select one**), as indicated on the outlet schedule.
		1. Front blades parallel to the long dimension.
		2. Front blades parallel to the short dimension.
	5. The frame shall be 16 gauge cold rolled steel construction, and the front blades and mullions shall be 14 gauge cold rolled steel construction.
3. Fastening:
	1. The grille shall be supplied with (**select one**):
		1. Countersunk screw holes complete with screws.
		2. No screw holes.
4. Paint Specification:
	1. Paint finish shall be (**select one**):
		1. Baked-on powder coat finish.
			1. The paint film thickness shall be a minimum of 2 mils.
			2. The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.
			3. The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.
			4. The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.
			5. The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.
		2. All components shall have a custom finish in a color to match a customer supplied sample.
5. Options:
	1. Opposed Blade Damper:
		1. The register shall be supplied with a coated steel (D) opposed blade damper. The damper shall be operable from the register face.

**2.03 Double Deflection Heavy Duty Adjustable Gym Grille**

1. Description:
	1. Furnish and install Price Model 920 heavy duty gym grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.
2. Construction:
	1. The grille blades and border shall be steel construction.
	2. The 14 gauge steel border shall have smooth contours to reduce the possibility of injury to occupants when installed in a gymnasium. The grille shall be suitable for surface mounting with 1-1/4 inch flat border.
	3. Grilles blades shall be single deflection, individually adjustable louver type.
	4. The front blades shall be adjustable from +/- 45 degrees degrees deflection, with 1/2 inch on center blade spacing.
	5. The rear blades shall be individual adjustable with 3/4 inch on center blade spacing.
	6. The grille blade orientation shall be (**select one**), as indicated on the outlet schedule.
		1. Front blades parallel to the long dimension.
		2. Front blades parallel to the short dimension.
	7. The frame shall be 16 gauge cold rolled steel construction, and the front deflection blades and mullions shall be 14 gauge cold rolled steel construction.
	8. The rear deflection blades shall be 24 gauge cold rolled steel.
3. Fastening:
4. The grille shall be supplied with countersunk screw holes complete with screws.
5. Paint Specification:
	1. Paint finish shall be (**select one**):
		1. Baked-on powder coat finish.
			1. The paint film thickness shall be a minimum of 2 mils.
			2. The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.
			3. The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.
			4. The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.
			5. The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.
		2. All components shall have a custom finish in a color to match a customer supplied sample.
6. Options:
	1. Opposed Blade Damper:
		1. The register shall be supplied with a coated steel (D) opposed blade damper. The damper shall be operable from the register face.

**PART 3 – EXECUTION**

**3.01 Examination**

1. Verify that conditions are suitable for installation.
2. Verify that field measurements are as shown on the drawings.

**3.02 Installation**

1. Install in accordance with manufacturer’s instructions.
2. See drawings for the size(s) and locations of grilles and registers.

**3.03 Field Quality Control**

1. See Section 01 40 00 – Quality Requirements for additional requirements.

**3.05 Cleaning**

1. See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

**3.06 Closeout Activities**

1. See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.
2. See Section 01 79 00 – Demonstration and Training for additional requirements.